| Inspection, Testing, and Maintenance Cover Sheet NFPA25 as amended by CCR, Title 19 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Property Information: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Name: | E&E CO LTD |  | Occupancy/Use: |  |  |  | B |  |  |  |  |  |  |  |
| Address: | 1680 Tide Ct. |  | Construction Type: |  |  |  | Type III-A |  |  |  |  |  |  |  |
| City: | Woodland |  | No. Stories: |  |  |  | 1 |  |  |  |  |  |  |  |
| ZIP: | 95776 |  | Year Constructed: |  |  |  |  |  |  |  |  |  |  |  |
| Contact: | Alex Gonzalez |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Telephone: | (16)-897-7622 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Contractor Information: |  |  |  |  |  | Number of System Risers 1 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Copy sent to: |  |  |  |  |  |  |  |
| Name: |  |  |  |  |  |  | Owner | Date: |  |  |  |  |  |  |
| Address |  |  |  |  |  |  | Fire AHJ | Date: |  |  |  |  |  |  |
| City: |  |  |  |  |  |  | Contractor | Date: |  | 1-8-26 |  |  |  |  |
| State: |  |  |  |  |  |  | NOTES: 1) For specific inspection, testing, and maintenance requirements and information, see NFPA 25, 2011 edition as amended by California Code of Regulations, Title 19, §901 to §906. 2) Inspection items may be performed by the owner in accordance with California Code of Regulations, Title 19, §904.1(a) |  |  |  |  |  |  |  |
| Telephone: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CA License#: | 905493 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Job #: | SV2511300328 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Performed by: | David Monachello |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check box for each system inspected and enter the number of forms used for inspection. Check boxes (Fail or Pass) to indicate status of inspected system at end of inspection. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Forms Included with this Report |  | NFPA 25 Chapter |  |  | Number of Forms |  |  |  | N/A |  |  | Fail* | Pass |  |
| Automatic Sprinkler System |  | 5 |  |  |  |  |  |  |  |  |  |  |  |  |
| Standpipe and Hose System |  | 6 |  |  |  |  |  |  |  |  |  |  |  |  |
| Private Water Supply System |  | 7 |  |  | 1 |  |  |  |  |  |  |  |  |  |
| Fire Pump |  | 8 |  |  |  |  |  |  |  |  |  |  |  |  |
| Water Storage Tank |  | 9 |  |  |  |  |  |  |  |  |  |  |  |  |
| Water Spray System |  | 10 |  |  |  |  |  |  |  |  |  |  |  |  |
| Foam Water Sprinkler System |  | 11 |  |  |  |  |  |  |  |  |  |  |  |  |
| Water Mist System |  | 12 |  |  |  |  |  |  |  |  |  |  |  |  |
| Concerns that are Not Deficiencies (i.e. Non-Sprinklered Areas) |  |  |  |  |  |  |  |  |  |  |  | Yes | No |  |
| *See "Deficiencies and Comments" section at end of each respective form. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Private Fire Service Main |  |  |  | California Code of Regulations - Title 19 Inspection, Testing, and Maintenance |  |  |  |  |  |  |  |  |  | Quarterly and Annual Report |  |  | 1 of 2 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Property Information |  |  |  |  |  |  |  |  | Contractor or Licensed Owner Information |  |  |  |  |  |  |  |  |  |  |
| Building Name |  |  | E&E CO LTD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Address |  |  | 1680 Tide Ct. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City |  |  | Woodland |  | License # |  | 905493 |  |  |  |  |  |  |  |  |  |  |  |  |
| Contact Person |  |  | Alex Gonzalez |  | SFM |  |  |  | Job # |  |  | SV2511300328 |  |  |  |  |  |  |  |
| Phone |  |  | (916)-897-7622 |  | CSLB |  |  |  | Misc. |  |  |  |  |  |  |  |  |  |  |
| Quarterly Inspections |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| I = Inspection T = Test M = Maintenance P = Pass F = Fail N/A = Not Applicable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item |  | Description |  |  |  |  |  | NFPA 25 CA ed. Reference |  |  | Date |  |  |  | Date | Date |  | Date |  |
|  |  |  |  |  |  |  |  |  |  |  | 1-8-26 |  |  |  |  |  |  |  |  |
| 1.1 | I | Control Valves – Identification Sign |  |  |  |  |  | 13.3.1 |  |  | P |  |  |  |  |  |  |  |  |
| 1.2 | I | Control Valves – Inspection |  |  |  |  |  | 13.3.2 |  |  | P |  |  |  |  |  |  |  |  |
| 1.3 | I | Hose Houses |  |  |  |  |  | 7.2.2.7 |  |  | N/A |  |  |  |  |  |  |  |  |
| 1.4 | I | Fire Department Connections |  |  |  |  |  | 13.7 |  |  | P |  |  |  |  |  |  |  |  |
| 1.5 | I | Pressure Reducing Valves |  |  |  |  |  | 13.5.1.1 |  |  | N/A |  |  |  |  |  |  |  |  |
| 1.6 | I | Backflow Preventers |  |  |  |  |  | 13.6.1 |  |  | P |  |  |  |  |  |  |  |  |
| 1.7 | I | Supervisory Devices |  |  |  |  |  | 13.3.3.5.1 |  |  | P |  |  |  |  |  |  |  |  |
| 1.8 | I | Monitor Nozzles |  |  |  |  |  | 7.2.2.6 |  |  | N/A |  |  |  |  |  |  |  |  |
| ANNUAL INSPECTION, TESTING, AND MAINTENANCE Include ALL Quarterly Inspections |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| I = Inspection T = Test M = Maintenance P = Pass F = Fail N/A = Not Applicable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item |  | Description |  |  |  | NFPA 25 CA ed. Reference |  |  |  | Date |  |  | Comments Only |  |  |  |  |  | P,F,N/A |
| 1.9 | I | Hydrants (Dry Barrel and Wall) |  |  |  | 7.2.2.4 Table 7.2.2.4 |  |  |  | 1-8-26 |  |  |  |  |  |  |  |  | F |
| 1.10 | I | Hydrants (Wet Barrel) |  |  |  | 7.2.2.5 Table 7.2.2.5 |  |  |  |  |  |  |  |  |  |  |  |  | N/A |
| 1.11 | I | Mainline Strainers |  |  |  | 7.2.2.3 Table 7.2.2.3 |  |  |  |  |  |  |  |  |  |  |  |  | N/A |
| 1.12 | I | Piping (Exposed) |  |  |  | 7.2.2.1 Table 7.2.2.1.2 |  |  |  | 1-8-26 |  |  |  |  |  |  |  |  | P |
| 1.13 | I | Piping (Underground) |  |  |  | 7.3.1 |  |  |  | 1-8-26 |  |  |  |  |  |  |  |  | P |
| 1.14 | I | Hose |  |  |  | NFPA 1962 |  |  |  |  |  |  |  |  |  |  |  |  | N/A |
| 2.1 | T | Control Valve – Position |  |  |  | 13.3.3.1 |  |  |  | 1-8-26 |  |  |  |  |  |  |  |  | P |
| 2.2 | T | Control Valve – Operation |  |  |  | 13.3.3 |  |  |  | 1-8-26 |  |  |  |  |  |  |  |  | P |
| 2.3 | T | Monitor Nozzles |  |  |  | 7.3.3 |  |  |  |  |  |  |  |  |  |  |  |  | N/A |
| 2.4 | T | Hydrants – Flush |  |  |  | 7.3.2 |  |  |  | 1-8-26 |  |  |  |  |  |  |  |  | P |
| 2.5 | T | Supervisory Devices |  |  |  | 13.3.3.5 |  |  |  | 1-8-26 |  |  |  |  |  |  |  |  | P |
| 2.6 | T | Backflow Preventer Assemblies |  |  |  | 13.6.2 |  |  |  | 1-8-26 |  |  |  |  |  |  |  |  | P |
| 2.7 | T | Pressure Reducing Valve (Partial Flow Test) |  |  |  | 13.5.1.3 |  |  |  |  |  |  |  |  |  |  |  |  | N/A |
| 3.1 | M | Control Valves |  |  |  | 13.3.4 |  |  |  | 1-8-26 |  |  |  |  |  |  |  |  | P |
| 3.2 | M | Mainline Strainers |  |  |  | 7.2.2.3 |  |  |  |  |  |  |  |  |  |  |  |  | N/A |

| Private Fire Service Main |  |  |  |  |  |  |  |  | California Code of Regulations - Title 19 Inspection, Testing, and Maintenance |  |  |  |  |  |  |  |  |  | Quarterly and Annual Report |  |  |  |  | 2 of 2 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Property Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Contractor or Licensed Owner Information |  |  |  |  |  |  |  |  |  |
| Building Name |  |  |  | E&E CO LTD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Name |  |  |  |  |
| Address |  |  |  | 1680 Tide Ct. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Job # |  | SV2511300328 |  |  |
| City |  |  |  | Woodland |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Misc. |  |  |  |  |
| ANNUAL INSPECTION, TESTING, AND MAINTENANCE Include ALL Quarterly Inspections |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| I = Inspection T = Test M = Maintenance P = Pass F = Fail N/A = Not Applicable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item |  |  | Description |  |  |  |  |  |  |  |  |  | NFPA 25 CA ed. Reference |  |  |  | Date | Comments Only |  |  |  |  |  |  | P,F,N/A |
| 3.3 | M |  | Dry Pipe Valve Interior Cleaned |  |  |  |  |  |  |  |  |  | 13.4.4.3.1 |  |  |  |  |  |  |  |  |  |  |  | N/A |
| 3.4 | M |  | Low Points in System Drained |  |  |  |  |  |  |  |  |  | 13.4.4.3.2 |  |  |  |  |  |  |  |  |  |  |  | N/A |
| 3.5 | M |  | Backflow Preventer |  |  |  |  |  |  |  |  |  | 13.6.3 |  |  |  | 1-8-26 |  |  |  |  |  |  |  | P |
| 3.6 | M |  | Obstruction Investigation Required (If “Yes”, see Deficiencies and Comments Section for Results.) |  |  |  |  |  |  |  |  |  | 14.3 |  |  |  |  | Yes No |  |  |  |  |  |  | N/A |
| 3.7 | M |  | System Returned to Service |  |  |  |  |  |  |  |  |  | 4.5.3 15.7 |  |  |  | 1-8-26 | Yes No |  |  |  |  |  |  | P |
| D = Deficiency C = Comment (Indicate type ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item |  | Date |  |  | Riser | D | C |  |  |  |  | Deficiencies and Comments Indicate all equipment, devices and parts that were repaired or replaced |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 1-8-26 |  |  |  |  | X | Flushed and Inspected (10) American Darling Valve 5 ¼ Dry Barrel Hydrants. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.19 |  | 1-8-26 |  |  |  | X |  | Hydrant behind building across from bay 23 and 24 unable to operate hydrant due to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Operating stem nut unable to turn recommend HCI Service investigate issue. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.19 |  | 1-8-26 |  |  |  | X |  | In Total (3) hydrants 4” cap unable to remove HCI Service to investigate issue. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | (Hydrant behind fire pump, Hydrant side of building past gate, and Hydrant across from |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Bay 23 and 24) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 1-8-26 |  |  |  |  | X | Unable to locate hydrant shutoffs for (3) hydrants recommend looking at original maps. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | (Hydrant Behing Fire Pump, Hydrant outside GD Fulfilment, and Hydrant side of building |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Past gate) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | End Of Reports |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check here if additional Deficiencies and Comments are listed on Form AES9. See Correction Form AES 10 for corrected deficiencies. |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Number attached |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Number attached |  |  |  |  |  |  |  |  |  |  |
| I hereby certify that the fire protection equipment listed above has been fully inspected, tested, and maintained on this date by the company indicated above, in accordance with CCR, Title 19, Sections 901 to 906 and that the equipment is fully operable except as noted in the “Deficiencies and Comments” section of this form. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Check box if Annual Inspection, Testing & Maintenance Items are Completed in the Indicated Quarter |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Quarter |  |  | 1st - Annual |  |  |  |  |  |  | 2nd - Annual |  |  |  | 3rd - Annual |  |  |  |  |  |  |  | 4th - Annual |  |  |  |
| Date |  |  | 1-8-26 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Print Name |  |  | David Monachello |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Signature |  |  | David Monachello |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |